TEMORA SHIRE COUNCIL

POLLUTION INCIDENT RESPONSE

MANAGEMENT PLAN

TEMORA SEWERAGE SCHEME

ACTIVE

Review Details

ABOUT THIS RELEASE

DOCUMENT NAME: 	Pollution Incident Response Management Plan – Temora Sewerage Scheme

AUTHOR:    			Temora Shire Council

ENDORSEMENT DATE:

REVIEW

| Revision Date | Revision Description |  | Date approved by Council | General Managers Endorsement |
| --- | --- | --- | --- | --- |
| 09/2016 | Initial Document |  |  |  |
| 05/2017 | General Review |  |  |  |
| 09/2019 | General Review |  |  |  |

PLANNED REVIEW

| Planned Review Date | Revision Description |  | Review by |
| --- | --- | --- | --- |
| 09/2021 | General Review |  |  |

Contents

1.	Introduction	4

2.	Scope	4

2.1	Objectives	4

3.	References	4

4.	Definitions	4

5.	Responsibilities	5

6.	Pollution Incident Response Management Plan	5

6.1	Sewerage Scheme Overview	5

6.2	Hazard and Risk Assessment	5

6.3	Incident Response	6

6.3.1	Pollution Incident	6

6.3.2	Incident Response Process Diagram	7

6.4	Community Notification	7

6.5	Incident Investigation	7

6.6	Pre-emptive Measures	8

6.6.1	Engineering Controls	8

6.6.2	Administrative Controls	8

6.7	Training	8

7.	Records Management	9

7.1	Location and Maintenance	9

8.	Review	9

9.	Appendices	9

Appendix A – Site Plans and Reticulation Network Map	10

Appendix B – Sewerage and Recycled Water Risk Assessment and Action Plan	13

Appendix C – Incident Response Process Diagram	19

Appendix D – Chemical Register	20

Appendix E – Personal Protective Equipment	20

Appendix F – Register of Identified Records	21

# Introduction

In February 2012 an amendment to the Protection of the Environment Operations Act 1997 introduced a requirement for all licensees to prepare and implement a Pollution Incident Response Management Plan (PIRMP) for each of its licensed activities in accordance with the requirements set out in Part 5.7A of the PEOA Act 1997.

This plan has been developed to document the processes required to prepare for and respond to pollution incidents at the Temora Sewage Treatment Plant (TSTP) and associated reticulation network and ensure that hazards to the environment, human health and safety are managed effectively.

# Scope

This PIRMP applies to all activities relating to Temora Sewage Scheme (EPA Licence No.2523).

# Objectives

The objectives of this plan are to;

- Ensure comprehensive and timely communication about a pollution incident to staff, the Environmental Protection Authority (EPA), other relevant authorities specified in the Act (NSW Ministry of Health, WorkCover NSW, Fire and Rescue and Council) and any persons who may be affected by the impacts of a pollution incident.

- Minimise and control the risk of a pollution incident occurring within the Temora sewerage scheme, by requiring identification of risk and the development of planned actions to minimise and manage those risks.

- Ensure the plan is effectively implemented by trained staff, identifying persons responsible for implementing it, and ensuring that the plan is regularly tested for accuracy, currency and suitability.

# References

EPA NSW Environmental Guidelines: Preparation of pollution incident response plans

Local Government Act 1993

Protection of the Environment Operations Act 1997

Protection of the Environment Operations (General) Regulation 2009

Public Health Act 1991

Water Administration Act 1986

TSC IMS EM-00 Environmental Aspects and Impacts Statement

# Definitions

Pollution incident is defined as, an incident or set of circumstances during, or as a consequence of which there is or is likely to be a leak, spill or other escape or deposit of a substance, as a result of which pollution has occurred, is occurring or is likely to occur. It includes an incident or set of circumstances in which a substance has been placed or disposed of on premises, but it does not include an incident or set of circumstances involving only the emission of any noise (see the POEO Act 1997).

Material harm to the environment is defined as, actual or potential harm to the health or safety of human beings or to ecosystems that is not trivial, or results in actual or potential loss or property damage of an amount, or amounts in aggregate, exceeding $10,000 (or such other amount as is prescribed by the regulations).

Loss is defined as, reasonable costs and expenses that would be incurred in taking all reasonable and practicable measures to prevent, mitigate or make good harm to the environment.

Immediately is defined as, promptly and without delay.

# Responsibilities

Directors are responsible to:

Ensure all workers are aware and are involved in developing this plan.

Ensure all workers are adequately trained in the operation of this plan.

Provide adequate resources to develop and manage this plan.

Managers are responsible to:

Provide for the implementation of this plan in their sections and area(s) of control.

Consult and communicate with workers ensuring they are familiar with this plan.

Ensure full staff compliance with this plan.

Participate in review of this plan as required.

Supervisors are responsible to:

Comply with this plan.

Ensure implementation of this plan in their section and area(s) of control.

Participate in review of this plan as required.

Provide training and supervision.

Workers are responsible to:

Co-operate with their manager / supervisor to ensure implementation and compliance with this plan.

Attend and participate in training relating to this plan.

Participate in review of this plan as required.

# Pollution Incident Response Management Plan

# Sewerage Scheme Overview

The original sections of the Temora Sewerage Scheme were constructed and commissioned in the late 1930’s with the original treatment plant having a design capacity of 5000EP. The scheme has been significantly augmented over the past 80 years and now consists of an 4500EP treatment plant, approximately 54km of reticulation main and 5 reticulation pump stations. The Temora STP currently treats approximately 720kL of sewage daily in dry weather, potentially reaching 4 times this flow during heavy rain periods. The current treatment process includes screening, primary sedimentation, aeration and retention.

# Hazard and Risk Assessment

Hazards and risks associated with activities of the Temora Sewerage Scheme causing potential material harm to human health or the environment include:

Sewage discharge (raw or partially treated), potentially be caused by;

- Storms (lightning/heavy rainfall/wind) causing power failure or infrastructure damage

- Reticulation blockages

- Damage to reticulation (contractors or other damage during excavations etc.)

- Infrastructure failure due to age

- Communications failure

- Level sensor failure

- Excessive flows

- Mechanical break down

- Power outage

- Treatment plant blockage

- Lagoon failure

- Sewerage reticulation network contamination (chemicals)

- Maintenance and or capital upgrade works

Chemical spill, potentially caused by:

- Delivery incident

- Inappropriate chemical use

- Fire

A Risk Assessment and Action Plan for the Temora Sewerage Scheme is located in Appendix B of this document.

# Incident Response

This section details the response requirements in the event of an incident.

# Pollution Incident

A pollution incident is required to be notified if there is a risk of ‘material harm to the environment’ that is not trivial.

If there is immediate threat to Human health or Safety, at first instance call triple zero “000” (“112” if using a mobile). Fire and Rescue NSW, the NSW Police and the NSW Ambulance Service are the first responders, as they are responsible for controlling and containing incidents.

If the incident does not require an initial combat agency, or once the 000 call has been made, the Manager of Works or Director of Engineering Services is to notify the relevant authorities ‘Immediately’ in the following order;

- EPA Environment Line (written report to be provided within 7 days)	131 555

- NSW Health 							02 9391 9000

- Work Cover 							13 10 50

- Fire & Rescue							1300 729 579

- Any other persons who may be affected by the incident - Land owners, businesses, sporting clubs, police, etc.

The 24 hour emergency number for Temora Shire Council is:

(02) 69 801100

Temora Sewerage Treatment Works emergency evacuation point is located at outside the compound at the front main access gate adjacent to the emergency evacuation point sign.

In all situations where there is damage and/or loss to private property or a member of the public due to an incident related to this plan contact:

Council’s Safety and Systems Coordinator (02) 69801100

# Incident Response Process Diagram

The incident response required depends on the type and severity of the incident that has occurred. A flow diagram is located in Appendix C of this plan detailing the sequence of response in the event of a sewage overflow / bypass for both minor and major incidents.

# Community Notification

Impacts on the community due to sewage distribution and treatment incidents are variable and depend on location, volumes of spills or other factors. Communication methods will be used on a case by case basis and in all situations Temora Shire Council staff will attempt to provide early warning to directly affected premises by phone call or site visit. Early warning is to include;

- Details on the nature and severity of the incident,

- How those affected can prepare and respond, and

- Provide important advice such as avoiding contact and use of affected areas.

Where early warning is not possible Temora Shire Council will provide notification and communication during and after an incident to advise those affected with information, advice and updates. Notification and communication methods will be determined on a case by case basis and may include the following;

- Phone calls

- Media releases (radio/television/newspaper/internet/social media as required)

- Site visits/door knocking

- Letter drops

- Warning signs

- Other methods as the situation requires

In the event of a major chemical or sewage spill into a waterway, Temora Shire Council will barricade and signpost areas of the affected waterway that may be used for recreational purposes. The signs are to warn the community of the contamination and advise them to avoid activities such as swimming until contamination has cleared.

Contaminated land is to be disinfected, ponded sewage pumped out and faecal coliforms are to be monitored until background levels are reached. Regular communication and notification of affected persons is to be provided until the incident and clean-up of the impacted site and affected areas have been completed.

# Incident Investigation

All pollutions incidents will be investigated by Councils Safety and Systems Coordinator. For all other incidents, the Engineering Works Manager will determine whether an incident investigation will be conducted. All sewerage overflow incidents must be recorded and reported to the Manager of Works using the Sewer Choke and Overflow Report form.

# Pre-emptive Measures

The first priority for pre-emptive measures in relation to a potential pollution incident is to eliminate hazards that pose a risk of causing a pollution incident. If this is not possible, other means of risk control such as substitution, engineering and, or administration shall be employed to mitigate the likelihood of a pollution incident occurring.

# Engineering Controls

The following pollution incident prevention features are currently operational within the Temora sewerage scheme;

- TSTP inlet works step screen has a high level bypass to prevent overflow.

- TSTP pump station has;

- Level sensors and an SMS/email alarm system to alert operators of failure or conditions that may result in an overflow.

- 2 sets of 2 x 8kw submersible pumps that have the ability to work independent of each other in the event of pump failure.

- A backup generator which automatically operates in the event of power failure.

- TSTP has 2 x primary sedimentation/aeration lagoons of which only one operates during the normal treatment process. Current TSC procedure is to ensure one of the primary lagoons is empty at all times, this allows an additional 20ML storage in the event there is a requirement to store untreated or partially treated sewerage prior to overflow of the retention lagoons.

- The remaining reticulation pump stations have rotating red beacons and sound alarms that activate in the event of overflow or power failure.

- Council water metres have backflow prevention devices fitted.

# Administrative Controls

Temora Shire Council undertakes monitoring and preventative maintenance to reduce the potential for incidents in all areas of the Temora Sewerage Scheme. This includes daily, weekly and longer term inspections, preventative maintenance and capital renewal works.

Council has one management staff member and one sewerage operator on call 24 hours a day 7 days per week. Access to staff on call is directed through the Council 24 hour emergency number listed in section 6.3.1.

Council currently lacks documented procedures and system forms associated with the above described activities, however this is an item included in the Risk Assessment and Action Plan and will be developed and implemented prior to the next review of this plan.

# Training

Managers, Supervisors, Gangers and relevant Workers, shall be provided induction training in this plan, and the use of associated forms.

Additionally, relevant staff will be involved in a biennial exercise / drill to test the implementation of the plan. In the event of a significant incident, an investigation and debrief will be conducted, documentation updated (if required) and staff will undertake re-induction training.

# Records Management

# Location and Maintenance

Copies of the PIRMP must be maintained at the following locations;

- TSTP (located at the main entrance in a water proof sleeve).

- Temora Council chambers, available to the public on written request, free of charge.

- Temora Shire Council website

- Sewerage operator work vehicle

Operational documents and identified records associated with this plan shall be stored and maintained in an adequate location. Details of document and record locations are listed in Appendix E of this plan.

Records must be:

- Stored and maintained for a period of 7 years,

- Be made available to authorised persons in compliance with legislative requirements.

# Review

This plan will be reviewed under the following circumstances;

- Biannually in September in conjunction with Councils EPA annual return submission,

- Following a change in legislation, or

- Following a reportable pollution incident, or

- Following the planned implementation of a new system, new technology or new process relating to the Temora sewerage scheme.

# Appendices

#### Appendix A – Site Plans and Reticulation Network Map

Inlet Works

Maturation Lagoons

Reticulation Network

#### Appendix B – Sewerage and Recycled Water Risk Assessment and Action Plan

| Ref No | Item / Activity /Process | Potential Hazard / Risk | Current Control Measures | Risk Class | Proposed Additional Risk Control / Action | Responsible Person | Date Completed | Residual Risk |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Management |
|  | System management | System failure Suspension of operation Legal action Human health incident Pollution incident Inability to respond to an emergency | Some management training undertaken Some policy and procedure in place | 1 | Engage a consultant to complete an audit/review of the current systems, and assist in developing up to date, holistic, comprehensive management framework relating to sewerage and recycled water operations at Temora Shire Council Investigate decoupling of the storm water/ recycled water systems (removal of Callaghan Park dam and Railway Dam from recycled water system) Develop Integrated Water Cycle Management Plan Develop Recycled Water Management Plan (RWMP) Develop Sewerage Scheme Strategic Business Plan | TSM TSM TSM TSM TSM | Audit/Review completed by GHD in 2017. IWCM underway with Public Works. RWMP will follow IWCM. | 2 |
|  | Staff training | Inadequate management of sewerage and recycled water system Pollution incident Human health incident Non-compliance with EPA licence conditions Unable to respond to major system failure | Recycled water short course training undertaken for all sewer and recycled water staff Sewer trainee undertaking certificate 3 in Water Operations | 1 | Develop specific sewerage and recycled water training plan for staff involved in sewerage and recycled water operation and management | SC / HR | No Action. | 2 |
|  | Financial management | Unsustainable system Non-compliance with regulatory authorities | Sewerage reserve fund Annual maintenance budget | 1 | MANEX to review TBL performance report Following system review, investigate and report on all areas of financial management of water and sewerage (fees & charges, income, expenditure, reserves, etc.) Note: Consider optional private work fee for work Council currently responds to following complaint that once investigated is not Councils responsibility. This is traditionally handed to local plumbers. | TSM TSM | IWCM underway. TBL reports improving. | 2 |
|  | WHS management | Suspension of operation Legal action Human health incident Pollution incident | Some WHS policy Some operational procedures | 1 | Staff immunisation audit/review and report recommendations WHS audit of all recycled water and sewerage operations (operational procedures, WHS forms, system signage, emergency response equipment, site security, etc.) Specific WHS action plan and development of WHS framework, procedures and system forms. | SC SC / TSM SC / TSM | Immunisation complete No Action SWMS Developed | 2 |
|  | Maintenance and Capital Work Quality | Assets not reaching design life Failing infrastructure Increased sewer chokes Pollution incident Human health incident | Experienced staff | 2 | Staff training in Australian Standard and Water Service Australia (WSA) codes Development of standardised Quality Work Methods for sewer and recycled water maintenance activities to ensure quality and consistency (standard drawings) | WM WM |  | 2 |
|  | EPA Licence pollution monitoring (sampling) control points faecal coliform non-compliance | Discharge of non-compliant recycled water Financial penalties Suspension of licence Inaccurate test results Human health incident | Chlorine disinfection of recycled water | 1 | Publishing of Council recycled water quality test data ensuring compliance with EPA guidelines Develop sampling procedures addressing sample quality and worker safety (Work Method and SWMS) Review and update EPA licence control points and utilisation areas to reflect current system Investigate treatment process effectiveness (currently don’t meet EPA pollutant limits) Determine retention time and any short circuiting of current treatment process (GHD Rec) | TSM SC / TSM TSM TSM TSM | Complete No Action IWCM IWCM IWCM | 2 |
|  | Sewerage Treatment Works |
|  | Sewerage contamination - trade waste and chemicals | Adversely affect treatment process at treatment works Reticulation network choking and potential damage | Trade waste policy | 2 | Audit of registered trade waste businesses - system maintenance (grease traps, etc.) Community awareness regarding the effects of trade waste (Letter to businesses, Narraburra news etc.) | DENV DENV | No Action No Action | 3 |
|  | Sewerage inflow monitoring | Non-compliance with EPA licence conditions | Flow monitoring from wet well levels (inaccurate) | 3 | Continuous volume monitoring in pump station line to primary ponds | TSM | Complete | 3 |
|  | Early treatment process monitoring | Non-compliant water | Nil | 1 | Develop early process water quality monitoring to enable responsiveness to treatment issues prior to there being no options at release | TSM | IWCM | 3 |
|  | Disinfection | Non-compliance with EPA licence conditions Human health incident | Nil | 1 | Assess the suitability of chlorine disinfection (UV may be a better option) Upgrade chlorine dosing shelter meeting EPA requirements (bunding, signage, cover) Connect the Airport effluent line to chlorine dosing system Develop water quality monitoring schedule following chlorine disinfection and develop emergency procedures for water quality exceeding critical limits | TSM SC / WM WM WM | IWCM No Action No Action RWMP | 2 |
|  | TSTP – General operation and maintenance | Non-compliance with EPA licence conditions Human health incident | Informal inspection | 1 | TSTP operation and maintenance procedures | TSM | No Action | 2 |
|  | Sewerage Reticulation Network |
|  | Reticulation network – age / condition | Structural failure Discharge of untreated sewerage Human health incident Pollution incident Council unable to fund replacement of network Unable to respond to major failure of network | Some CCTV inspection undertaken Council has some funds in reserve | 1 | CCTV inspection and asset condition rating Defect identification, classification and GPS mapping using reflect defect management software Audit / review of asset valuation, condition, remaining useful life, current replacement costs | TSM TSM TSM | Ongoing Complete Complete | 2 |
|  | Storm water ingress | Treatment bypass at treatment works Discharge of untreated sewerage Treatment works pump station flooding Inadequate retention time at treatment works Human health incident Pollution Incident Overloading of reticulation network | Nil | 2 | Investigate flow monitoring at both treatment works and throughout reticulation network at critical junctions Manhole maintenance program (lid replacement, joint sealing, replacement, etc.) | TSM WM | No Action No Action | 3 |
|  | Reticulation network preventative maintenance | Increased main chokes Human health incident Pollution incident Network structural damage Limited knowledge of network condition | Some foaming completed in previous years | 2 | Develop routine preventative maintenance program including; Jetting (mains and service junctions where required) Foaming Combination cleaning / de-silting CCTV inspection Smoke testing | WM | Ongoing | 3 |
|  | Reticulation network mapping and access – (buried manholes) | Unable to access network for inspection, preventative maintenance, chokes, emergencies, etc. Unable to locate unmapped network | GIS map layer available (accuracy is only fair) | 2 | Review procedure for main extension relating to work as executed plans by both Council and third parties Record where it is assumed manholes are buried and/or unserviceable Gradual audit and update of GPS coordinates for network manholes using GPS survey | DENV TSM WM | No Action No Action Ongoing | 3 |
|  | Sewer choke maintenance | Discharge of untreated sewerage Pollution incident Human health incident | Confined spaces procedure | 2 | Develop sewer choke operational procedure and SWMS, including clean-up of any discharge Investigate purchase of emergency response equipment Develop electronic sewer choke register including GPS mapping | SC / WM SC / TSM TSM | Complete No Action Complete | 2 |
|  | Reticulation pump stations – maintenance and communication | Discharge of untreated sewerage Pollution incident Human health Incident Odour complaints Unable to respond to major failure | 3 of 4 pump station have some type of warning system. Treatment works pump station has SMS/Email alert of potential issues (high level, failure, etc) Airport pump stations have sound alarm and rotating beacon | 1 | Develop an operation and maintenance plan specifically for Council pump stations Investigate installation of SMS/Email warning for all pump stations | TSM TSM | No Action Ongoing | 3 |
|  | Recycled Water Reticulation Network |
|  | Effluent/Stormwater Storage dams | Non-compliance with NSW Office of Water Public health Incident | Aeration at Gardener street dam Fountain at Browns dam Monthly water quality testing undertaken 15/16 budgeted roll out of 2 x UV disinfection units to Gardener street and Railway dam. | 1 | Investigate improved pre-treated water quality (dam flocculation, carp eradication, rock lining of storage dams, etc.) Rectify bank erosion (rock lining) | TSM TSM | Ongoing Ongoing | 2 |
|  | Irrigation Pump Stations | Pollution incident Human health Incident Odour complaints Unable to respond to major failure | Sheltered Ad hoc maintenance Progressively upgraded | 1 | Develop operation and maintenance manuals specifically for Council irrigation pump stations Complete progressive upgrade of pump stations (shelters, VFD pumps, chlorine dosing, etc) Investigate energy saving initiatives | TSM TSM TSM | No Action Ongoing Ongoing | 2 |
|  | Third party use of recycled water | Non-compliance with NSW Office of Water Public health Incident Legal action against Council | Some third parties connected to Council pump lines where some filtration is taking place | 1 | Develop and implement legal agreements with third party users Review third party pumping arrangements (Council pump or private pump). Where possible bring third party onto Council system. Electronic flow monitoring, water filtration/disinfection. Where private pumping is undertaken investigate electrical arrangements (Council paying for power) Audit of current third party end use, including procedures and control measures | TSM TSM TSM TSM | No Action IWCM Complete RWMP | 2 |
|  | Backflow prevention | Human health incident Non-compliance with NSW Office of Water | Back flow prevention devices in place at Council utilisation areas Testing undertaken annually in November | 1 | Audit Council utilisation areas ensuring water meters have backflow prevention devices fitted | TSM | Complete | 2 |
|  | Irrigation | Human health incident Non-compliance with NSW Office of Water | Off peak irrigation | 1 | Review current non treatment barriers End point water quality testing Develop irrigation time table and utilise automated afterhours irrigation of parks and gardens Operation and maintenance procedure for irrigation network (line cleaning, valve maintenance, sprinkler maintenance, etc.) GPS locate and map irrigation network | TSM TSM TSM TSM TSM | RWMP RWMP RWMP No Action Underway | 2 |
|  | Soil analysis | Environmental Harm | Nil | 2 | Receiving environment soil analysis to determine the capability of the soil receiving nutrients, metals and salts. (GHD Rec) | TSM | Complete | 2 |

#### Appendix C – Incident Response Process Diagram

MAJOR

MINOR

#### Appendix D – Chemical Register

| Name | Manufacturer | Maximum Volume Stored | Location |
| --- | --- | --- | --- |
| Chlorine | Orica | 2000L | TSTP |
| Diesel | BP | 100L | Backup Generator |
| Unleaded Fuel | BP | 40L | Jetting Machine |
| Disinfectant | Rivchem | 40L | Depot |
| Sewercide | Momar | 40kg | Depot |
| Rootex | Momar | 500g | Depot |
| Hydro Clean | Momar | 75L | Depot |
| Oil | BP | 20L | Depot |
| Glyphosate | Nufarm | 20L | Depot |

#### Appendix E – Personal Protective Equipment

| PPE | Location Stored |
| --- | --- |
| Hearing protection | Depot store / plumbers truck |
| Sunscreen | Depot store / plumbers truck |
| Gloves – rubber, leather and material | Depot store / plumbers truck |
| Gumboots | Depot store |
| Disposable overalls | Depot store |
| Face masks | Depot store |
| Safety sunglasses / Safety goggles | Depot store / plumbers truck |
| First aid kit | Depot store / plumbers truck |
| Gas monitor | Plumbers truck |
| Fall arrest system | Depot store |
| Safety clothing (hi-vis, long pants, long sleeves) | Issued to staff |
| Steel capped boots | Issued to staff |

#### Appendix F – Register of Identified Records

| Item | Location |
| --- | --- |
| EPA - Environmental Protection License | EPA website, TSTP, work vehicle and Council website |
| Pollution Incident Response Management Plan (PIRMP) | TSTP, work vehicle and Council website |
| Council Policy and Procedure | Council website |
| TBL Sewerage Performance Report | NSW office of water online portal |
| EPA Annual Return | Recorded in TRIM |
| TSTP Inflow Monitoring | Centratech Systems IRRInet online portal |
| TSTP Outflow monitoring (pumped and overflow) | Centratech Systems IRRInet online portal |
| Third Party Water Delivery Records |  |
| Third Party User Agreements |  |
| Water Quality Monitoring Records | T:\engineering works\ water and sewer, and displayed in accordance with EPA requirements for publishing pollution monitoring data |
| Backflow Prevention Inspection Reports | Councils network drive T:\engineering works\ water and sewer |
| Training Records | Councils network drive T:\business services\human resources\payroll\staff training |
| Safety Data Sheets | Smart SDS software program |
| Equipment Maintenance Records |  |
| Choke, Bypass, Overflow Records | Councils network drive T:\engineering works\ water and sewer |
| Capital and Maintenance Work Records | Councils network drive T:\engineering works\ water and sewer |
| Sewerage Scheme Management Plan |  |
| Recycled Water Scheme Management Plan |  |
| Operation and maintenance manuals |  |
| Sewerage Asset Register | T:\Engineering Works\Administration & Legislative\Asset Management\Sewer\Asset Sheet & Revaluation |

# Text boxes

OPERATOR TO ASSESS THE INCIDENT

NOTIFY SAFETY OFFICER OR MANAGER OF WORKS

FOR DETERMINATION OF POLLUTION INCIDENT (Cl. 6.2)

IS THE SURCHARGE

OR SPILL A MAJOR OR

MINOR INCIDENT?

MINOR

MINOR

SECURE THE SITE,

ENSURE SAFETY OF

STAFF AND PUBLIC AND PLAN SITE CLEAN-UP (Cl 6.2)

GAIN CONTROL OF

SITE AND COMMENCE

CLEANUP

NOTIFY EPA AND OTHER

RELEVANT STAKEHOLDERS

IMMEDIATELY (Cl. 6.2)

GET ADDITIONAL

ASSISTANCE IF

REQUIRED

COMMENCE SITE CLEAN-UP AND UNDERTAKE SAMPLING IF REQUIRED (Cl. 6.2)

COMPLETE SITE

CLEANUP

COMPLETE SITE CLEANUP

AND RECORD DETAILS

OF EVENT EG. DURATION,

VOLUMES, ACTIONS TAKEN ETC. (Cl 6.2)

COMPLETE SEWER CHOKE/OVERFLOW FORM AND RETURN TO SUPERVISOR (Cl 6.4)

COMPLETE AN INCIDENT REPORT AND SUBMIT TO EPA (Cl 6.2)